## Heat Load Area Sheet
Name of Project: | INDIRA GANDHI INSTITUTE |  |  |  |  | Job ref./ Enquiry No.:
Address: | GOREGAON |  |  |  |  | Estimated by: | GDK |  | Heat load for: | Summer
Space used for: | SEMINAR HALL No 1 |  |  |  |  | Peak load at: | 4.00 PM
Area in sq.ft = | 935 | Length in Ft. |  | Height in ft.= | 22 |  |  | DESIGN CONDITIONS
Volume in cu.ft | 20570 | Width in Ft. |  | Contact factor : | 0.88 | (British Units) | DBT | % RH | WBT | Gr/lb
Bypass factor : | 0.12 |  |  | Btu/hour |  | Outside | 95 | 60 | 83 | 151
| Area x | Temp.diff. x | Factor = | Sensible Load | Latent Load | Inside | 73 | 55 | 62 | 69
SOLAR GAIN-GLASS | [5 empty] | Difference | 22 | xxxx | xxxx | 82
Glass (N) | 0 | 11 | 0.56 | 0 | - | Eq. Temp.correction factor |  |  | 10
Glass (E) | 37.5 | 11 | 0.56 | 231 | - |  |  | OUTDOOR AIR (CFM)
Glass (S) | 0 | 11 | 0.56 | 0 | - | 90 | People x | 5.6233 | CFM/Person = | 506.1
Glass (W) | 0 | 165 | 0.56 | 0 | - | 1 | No. of air changes/hr |  | = | 342.8333
Glass (NE) | 0 | 11 | 0.56 | 0 | - | Selected Outdoor Air CFM = |  |  | 506.1
Glass (SW) | 0 | 113 | 0.56 | 0 | -
Glass (NW) | 0 | 118 | 0.56 | 0 | - |  |  | APPARATUS DEW POINT
Glass (SE) | 0 | 11 | 0.56 | 0 | -
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [5 empty] | Effective Sens. Heat Factor (ESHF) = ERSH/ERTH = |  |  |  | 0.76808
Wall (N) | 585.2 | 14 | 0.35 | 2867.48 | -
Wall (E) | 1326.5 | 28 | 0.35 | 12999.7 | - | INDICATED ADP = |  | 55 | SELECT.ADP= | 55
Wall (S) | 0 | 26 | 0.35 | 0 | -
Wall (W) | 0 | 22 | 0.35 | 0 | - |  | DEHUMIDIFIED AIR QUANTITY
Wall (NE) | 0 | 20 | 0.35 | 0 | -
Wall (SW) | 0 | 24 | 0.35 | 0 | - | Dehum. Rise = Contact Factor x (Rm Temp. - ADP)= |  |  |  | 15.84
Wall (NW) | 0 | 16 | 0.35 | 0 | - | Dehum. CFM = ERSH/1.08/Dehum. Rise = |  |  |  | 4753.4781
Wall (SE) | 0 | 28 | 0.35 | 0 | - |  | Dehum CFM /400 = |  |  | 11.8837
Exposed Roof | 935 | 45 | 0.48 | 20196 | - | U-factors: |  |  | Roof Insl | 0.12
TRANSMISSION GAIN-EXCEPT WALLS & ROOF | [5 empty] | Exposed Walls | 0.35 |  | Roof Non Insl | 0.48
All Glass | 37.5 | 22 | 1.13 | 932.25 | - | Partition Walls | 0.4 |  | Ceiling | 0.48
Partition Wall | 0 | 17 | 0.4 | 0 |  | Partition Glass | 0.43 |  | Floor | 0.48
Partition Glass | 0 | 17 | 0.43 | 0 | - | Factors for Glass: |  |  | Solar gain | 0.56
Ceiling | 0 | 17 | 0.48 | 0 | - |  |  |  | Transm. Gain | 1.13
Floor | 0 | 17 | 0.48 | 0 | - | Some typical inside design conditions:
INTERNAL HEAT | [5 empty] | DESIGN CONDITIONS | DBT | % RH | WBT | Gr/lb
People | 90 | 276 | 224 | 24840 | 20160 |  | 70 | 50 | 58.5 | 54.8
Lights (I) - W | 1870 | 3.41 | 1 | 6376.7 | - |  | 70 | 55 | 59.7 | 60.1
Lights (F) - W | 0 | 3.41 | 1.25 | 0 | - |  | 72 | 50 | 60.1 | 58.8
Equip.Load -W | 750 | 3.41 | 1 | 2557.5 | - |  | 72 | 55 | 61.4 | 64.4
-do- in HP | 0 | 2545 | 1 | 0 | - |  | 74 | 50 | 61.8 | 62
Others |  |  |  | 0 | 0 |  | 74 | 55 | 63 | 68
Subtotals |  |  |  | 71000.63 | 20160 |  | 75 | 50 | 62.6 | 65
Safety Factors (12.5% & 5% respectively) |  |  |  | 8875.0788 | 1008 |  | 75 | 55 | 64 | 71.5
Room Sensible & Latent Loads |  |  |  | 79875.7088 | 21168 |  | 76 | 55 | 64.9 | 74
[7 empty] | 77 | 55 | 65.6 | 76.6
Outdoor Air | cfm = | 506.1 |  | 1442.9923 | 3386.4163 |  | 90 | 88 | 86 | 184
Effective Room Sensible Heat (ERSH) |  |  |  | 81318.7011 | - |  | 104 | 45 | 83 | 138
Effective Room Latent Heat (ERLH) |  |  |  | - | 24554.4163 |  | 105 | 40 | 83 | 136
Effective Room Total Heat (ERTH) |  |  |  | 105873.1174 |  |  | 110 | 25 | 78 | 94
OUTDOOR AIR (O.A.)
Sensible Load |  |  |  | 10581.9437 | - | Air on Coil in deg F: |  |  | Check figures:
Latent Load |  |  |  | - | 24833.7197 | DBT : | 75.3423 |  | sq.ft/TR = | 77.0989
Effective Room Total Heat + O.A Heat |  |  |  | 141288.7808 |  | WBT : | 64.2359 |  | cfm/sq.ft = | 5.0839
Other Heat Gains @ 3% |  |  |  | 4238.6634 |  |  |  |  | cfm/TR = | 391.9655
GRAND TOTAL HEAT |  |  |  | 145527.4442 |  | TMBH = | 145.5274
|  |  | TR | 12.1273 |  | SMBH = | 91.9006 |  | Sheet No.

## Summary
SUMMARY OF HEATLOAD FOR INDIRA GAHDI INSTITUTE.
DATE : 09.04.2014 | [5 empty] | AREA / TR
SEMINAR HALL No 1 | Area in sq.ft = | 935 | TR | 12.1273 | 12.1273 | 77.0989
| Height in ft.= | 22 | Dehum CFM | 4753.4781
| People | 90 | Dehum CFM /400 = | 11.8837
| Equip.Load -W | 750
TOTAL | Area in sq.ft = | 935 | TR | 12.1273 | 12.1273 | 77.0989
| People | 90 | Dehum CFM | 4753.4781
| Equip.Load -W | 750 | Dehum CFM /400 = | 11.8837